## v.4.07.10 v1
Variables overview dynamx™
v.4.07.10 | [5 empty] | NA = Not Applicable | [12 empty] | v.1.61
-1 = Empty / No Default Value
CATEGORIES |  | VARIABLES | [9 empty] | MODBUS RTU |  |  |  | BACNet / MSTP |  |  | dxLink21 APP
Main | Level | Name | Short name | Public | Valid range | Default | Unit | EN ǀ Resolution/values | EN ǀ Description | Volatile | R/RW | Var Type | Address (start) | Address (end) | Data Type | Object Type | Object Number | Access Type | Belparts Key | Client Key | In Log
01. Mode | Basic | Actuator type | Actua type | Factory | 0..4 | NA | NA | 0 = Thermal PWM actuator 1 = Thermal 0..10Vdc actuator 2 = Electrical PWM actuator 3 = Electrical 0..10Vdc actuator 4 = Stepper | Factory setting of the actuator type. This has mainly an impact on the loop behavior. | C | R | Input Register | 54 |  | uint
01. Mode | Basic | Climate Status | ClimStatus | User | 0..5 | 2 | NA | 0 = Heating 1 = Cooling 2 = Not defined 3 = Error 4 = Check flow 5 = Flush mode | Reflects the status of the current operating mode. - Heating (0) : valve controls on Vsh - Cooling (1) : valve controls on Vsc - Not Definied (2) : neutral state (no heating, nor cooling requested) - Error (3) : is activated on DXMB4 if 'Check Flow' is not correct - Check Flow (4) : zero flow check Vam when DXMB4 is executing change/over - Flush mode (5) : the valve is in fully open position | V | R | Input Register | 56 |  | uint | Multistate Value | 1 | Present Value | R | R | Yes
01. Mode | Advanced | Integrator | Integr. | Factory | -32768 .. 32767 | 0 | NA | 1 | Control loop integrator value. | V | RW | Holding Register | 15 |  | sint
01. Mode | Advanced | Adaptive gain | U2 | Factory | -32768 .. 32767 | NA | NA | 1 | Momentary gain of adaptive gain algorithm. | V | R | Input Register | 82 |  | sint
01. Mode |  | Change/Over Control | C/O Ctrl | User | 0..1 | 0 | NA | 0 = Inactive 1 = Active | Defines whether the valve will automatically change/over (C/O) from heating mode to cooling mode and vice-versa based on the water temperature from the integrated ΔT measurement (Tam1 & Tam2). Note 1 - when using this function, please make sure that the Treturn variable is set correctly! Note 2 - this function is available for all product series, except for 6-port valves (DNX6) or Quattro valves (DXMB4). | W | RW | Output Coil | 15 |  | bool | Binary Value | 10 | Present Value | RW | RW | Yes
01. Mode |  | Control characteristic | Ctrl char | User | 0..1 | 1 | NA | 0 = Linear 1 = Equal percentage | Defines whether the control characteristic, i.e. the relation between Y1 and Vsh / Vsc (the flow setpoints in heating and cooling), is linear (0) or equal percentage (1). | W | RW | Holding Register | 14 |  | uint | Multistate Value | 4 | Present Value | RW | RW | Yes
01. Mode |  | Control Signal | Ctrl Sig | User | 0..1 | 0 | NA | 0 = Analog mode 1 = Digital mode | Sets the control input of the valve to analog or digital. - Analog mode (0): the valve is controlled through a single analog input signal Y1, typically from the output of a HVAC-controller - Digital mode (1): the valve receives its setpoint via the RS485 bus communication or the Bluetooth interface For a device with IRC-functionality (Integrated Room Control) Control Signal determines whether Tsetadj is being read from analog input Text1 (Texternal 1) or can be written via RS485 bus communication (digital) or the Bluetooth interface (digital). Note - after the setting of Ctrl Signal (0) is changed, the control loop state is reset. | W | RW | Output Coil | 0 |  | bool | Binary Value | 0 | Present Value | RW | RW | Yes
01. Mode |  | Flush | Flush | User | 0..1 | 1 | NA | 0 = Inactive 1 = Active | Used with 2- and 3-port valves When activated, this variable Flush forces the valve into its fully open position. - Active (1) : the valve is controlled to its fully open position, regardless of the input control signal. - Inactive (0) : the valve is in automatic control modus, defined by Climat Status. Note - as the Flush functionality is different for change/over applications (like 6-port valves and Quattro valves), the Flush is defined through another variable. Please refer to Flush 6Way. | W | RW | Output Coil | 8 |  | bool | Binary Value | 2 | Present Value | RW | RW | Yes
01. Mode |  | Flush 6Way | Flush 6Way | User | 0..2 | 0 | NA | 0 = Inactive 1 = Flush cooling 2 = Flush heating | Used with 6-port valves and Quattro valves When activated, this variable Flush 6Way forces the 6-port valve (or the Quattro valves) into its (their) fully open position on the cooling or on the heating port(s). The Flush 6Way parameter replaces the Flush variable, which is used for 2- and 3-port valves. - Inactive (0) : the valve is in automatic control modus, defined by Climat Status. - Flush cooling (1) : the valve is controlled to its fully open position on the cooling port*, regardless of the input control signal. - Flush heating (2) : the valve is controlled to its fully open position on the heating port*, regardless of the input control signal. * Note: the default cooling and heating port may be modified by the PortConnection variable | W | RW | Holding Register | 76 |  | uint | Multistate Value | 3 | Present Value | RW | RW | Yes
01. Mode |  | Measurement Signal | Meas Sig | User | 0..1 | 0 | NA | 0 = Analog mode 1 = Digital mode | This variable defines how the actual room temperature is received by the valve with IRC-functionality (Integrated Room Control). - Analog mode (0) : the valve expects the actual measured value for Troom from an external analogue input signal. - Digital mode (1) : values for Troom will be defined via the RS485 bus communication or via the Bluetooth interface. Note - for valves with ITC-functionality (Integrated Temperature Control) the Troom variable is used for the measured water temperature. | W | RW | Output Coil | 17 |  | bool | Binary Value | 1 | Present Value | RW | RW | Yes
01. Mode |  | Open loop | Open loop | User | 0..1 | 0 | NA | 0 = Closed loop 1 = Open loop | Used with 2- and 3-port valves This variable enables or disables the flow control loop. - Closed loop (0): the valve will be operated by the flow control loop and will therefore behave as a pressure independant control valve. - Open loop (1): the valve will operate as a standard modulating valve. The valve will follow the 0..10Vdc input signal and drives the valve correspondingly in a 0..100% position. Note - this function is not available on the 6-port valves, nor Quattro valves. | W | RW | Output Coil | 6 |  | bool | Binary Value | 9 | Present Value | RW | RW | Yes
01. Mode |  | System Type | Sys type | User | 0..7 | NA | NA | 0 = Heating 1 = Cooling 2 = DuoClim 4P 3 = Room or T° control heating 4 = Room or T° control cooling 5 = RC DuoClim 6 = Dp heating 7 = Dp cooling | The Sys type variable determines in which mode the valve will operate. - Heating (0) : sets the 2- or 3-port valve to operate in Heating modus and will thereby control the flow to the Vsh setpoint - Cooling (1) : sets the 2- or 3-port valve to operate in Cooling modus and will thereby control the flow to the Vsc setpoint - DuoClim 4P : sets the operation to dual climate 4-pipes systems, and therefore typically used with 6-port or Quattro valves - Room or T°control Heating (3) : IRC- or ITC-functionality in combination with 2- or 3-port valves to operate in Heating modus - Room or T°control Cooling (4) : IRC- or ITC-functionality in combination with 2- or 3-port valves to operate in Cooling modus - RC DuoClim (5) : IRC Room control in combinatiion with 6-port valves - êp heating (6) : êp-functionality in combination with 2- or 3-port valves to operate in Heating modus - êp cooling (7) : êp-functionality in combination with 2- or 3-port valves to operate in Cooling modus Note - depeding on the System Type, the control loop will result in a Climat Status Heating or Cooling which will determine whether the energy consumption will be added to the heating energy variable EnerHeat or the cooling energy variable EnerCool | W | RW | Holding Register | 25 |  | uint | Multistate Value | 0 | Present Value | RW | RW | Yes
02. Device |  | Area | Area | User |  | NA | sq in mm² | GPM (US): 0,001 Other: 1 | The inner area of the pipe. | C | R | Input Register | 26 |  | uint
02. Device |  | DN value | DN | User | GPM (US): 0,375..6 Other: 15..200 | NA | NPS inch DN mm | GPM (US): 0,001 Other: 1 | The normalized NPS or normalized DN-size of the pipe (depending on Vunit). | C | R | Input Register | 25 |  | uint
02. Device |  | KVS value | KVS | User |  | NA | cf. Vunit m³/h or US Gpm | 0.01 | The Kvs- or Cv-value of the device (depending on Vunit): - Cv-value for US Gpm - Kvs-value for all other units | C | R | Input Register | 50 | 51 | uint32
02. Device |  | Port Connection | Port Conn | User | 0..1 | 0 | NA | 0 = Port 1 Cool - Port 2 Heat 1 = Port 1 Heat - Port 2 Cool | This Port Connection variable is used with 6-port valves only - Port 1 Cool / Port 2 Heat (0) : defines Port 1 for Cooling (connections 1 + 4 = left side if the base of the T-shape = the common port is pointing to you) and Port 2 for Heating (connections 5 + 6 = right side if the base of the T-shape = the common port is pointing to you). - Port 1 Heat / Port 2 Cool (1) : defines Port 1 for Heating (connections 1 + 4 = left side if the base of the T-shape = the common port is pointing to you) and Port 2 for Cooling (connections 5 + 6 = right side if the base of the T-shape = the common port is pointing to you). Note - for more information on the mechanical connections of the 6-port valves, please refer to the "Port connections 6-port" section. | W | RW | Output Coil | 16 |  | bool |  |  |  | RW | RW | Yes
02. Device |  | Position of Return Temperature sensor | Treturn | User | 0..1 | 1 | NA | 0 = Tam1 on supply 1 = Tam1 on return | This parameter is used to determine which of both temperature sensors is used to measure the supply water temperature and which one is used to measure the return water temperature. - Tam1 on supply (0) : the Tam1 sensor (red labelled) is mounted in the supply part of the circuit - Tam1 on return (1) : the Tam1 sensor (red labelled) is mounted in the return part of the circuit | W | RW | Output Coil | 7 |  | bool | Binary Value | 8 | Present Value | RW | RW | Yes
02. Device |  | Nominal Flow | Vnom | User |  |  |  |  | Nominal flow value of the valve | V | R | Input Register | 104 | 105 | float
02. Device |  | Flow resolution range | Vrange | User | 0..4 | NA | NA | Vrange → Number of decimals (Vunit = 0, default) Vrange = 0 → 0,0001 Vrange = 1 → 0,001 Vrange = 2 → 0,001 Vrange = 3 → 0,01 Vrange = 4 → 0,1 | Selects the range and resolution of variable Vnom in order to aid the fixed point calculations of floating point number. For more detailed information, follow the link to the Vrange Table. | C | R | Input Register | 73 |  | uint
02. Device |  | Device Free Text | DeviceFreeText | User | 20 text characters | -1 | NA | 1 character | 20 characters that can be set as free text | W | RW | Holding Register | 301 | 310 | string |  |  |  | RW | RW | Yes
02. Device |  | Device Location | DeviceLocation | User | 12 text characters | -1 | NA | 1 character | 12 characters to specify the location of the BACNet device | W | RW | Holding Register | 327 | 332 | string |  |  |  | RW | RW | Yes
02. Device |  | Device Name | DeviceName | User | 12 text characters | -1 | NA | 1 character | Device Name for BACnet Devices | W | RW | Holding Register | 320 | 326 | string |  |  |  | RW | RW | Yes
02. Device |  | Production_Number | Production_Nb | User | 12 text characters | -1 | NA | 1 character | 12 characters to specify a customer productionnumber | W | RW | Holding Register | 387 | 392 | string |  |  |  | RW | RW | Yes
02. Device |  | Object Identifier | ObjectIdentifier | User | 0.. 4194303‬ | -1 | NA | 1 | Unique Identifier of a BACnet Device | C | RW | Holding Register | 85 | 86 | uint32 | Network Port | - | - | RW | RW | Yes
02. Device |  | Object Name | ObjectName | User | 20 text characters | -1 | NA | 1 character | Object Name for BACnet Devices | W | RW | Holding Register | 311 | 319 | string | Network Port | - | - | RW | RW | Yes
02. Device |  | Product Type | ProdType | User | Free text | NA | NA | 20 byte string, A..Z/0..9 | ASCII representation of Hardware Version of the device = HW type & revision number | C | R | Input Register | 5 | 14 | Free Text |  |  |  | R | R | Yes
02. Device |  | Serial Number | SN | User | Free text | NA | NA | 10 byte string, A..Z/0..9 | ASCII representation of the Serial Number of the device | C | R | Input Register | 0 | 4 | Free Text |  |  |  | R | R | Yes
02. Device |  | Software/Firmware version | SW rev | User | Free text | NA | NA | 20 byte string, A..Z/0..9 | ASCII representation of Software Version of the device = SW type & revision number | C | R | Input Register | 15 | 24 | Free Text |  |  |  | R | R | Yes
03. Signals |  | ADC Calibration X1 (10V) | ADC_Val_X1_10V | Factory | 0..65535 | NA | NA | 1 | Calibration Value X1 for 10V. Written during production. | W | R | Input Register | 57 |  | uint
03. Signals |  | ADC Calibration Y1 (0V) | ADC_Val_Y1_0V | Factory | 0..65535 | NA | NA | 1 | Calibration Value Y1 0V. Written during production. | W | R | Input Register | 96 |  | uint
03. Signals |  | ADC Calibration Y1 (10V) | ADC_Val_Y1_10V | Factory | 0..65535 | NA | NA | 1 | Calibration Value Y1 10V. Written during production. | W | R | Input Register | 97 |  | uint
03. Signals |  | ADC Calibration Y2 (0V) | ADC_Val_Y2_0V | Factory | 0..65535 | NA | NA | 1 | Calibration Value Y2 0V. Written during production. | W | R | Input Register | 98 |  | uint
03. Signals |  | ADC Calibration Y2 (10V) | ADC_Val_Y2_10V | Factory | 0..65535 | NA | NA | 1 | Calibration Value Y2 10V. Written during production. | W | R | Input Register | 99 |  | uint
03. Signals |  | FSK | FSK | Factory | -1..583 | NA | NA | 1 | Counter for number of motor rotations on CB04-board with Stepper-motor. After initialisation for 2-port and 3-port valves : - the value "-1" corresponds to the closed position ( A  AB : 0% ) - the value "583" corresponds to the open position ( A  AB : 100% ) After initialisation for 6-port valves : - the value "-1" corresponds to the open position to Port 1 - the value "583" corresponds to the open position to Port 2 | C | R | Input Register | 72 |  | uint
03. Signals |  | Output X1 | X1 | User | X1min..X1max | NA | Volt (dc) | 0.1 | This value represents the actual value of the analog output signal X1 (0..10Vdc). Depending on setting X1 type, this output can give different signals which can be used as feedback or control of other devices. Default it indicates the actual measured flow rate. | V | R | Input Register | 93 |  | uint | Analog Output | 0 | Present Value | R | R | Yes
03. Signals |  | X1 max | X1 max | User | 0..10 | 10 | Volt (dc) | 0.1 | The maximum value of X1 representing maximum flow / Δp / Y2 | W | RW | Holding Register | 71 |  | uint |  |  |  | RW | RW | Yes
03. Signals |  | X1 min | X1 min | User | 0..10 | 0 | Volt (dc) | 0.1 | The minimum value of X1 representing NO flow / Δp / Y2 | W | RW | Holding Register | 70 |  | uint |  |  |  | RW | RW | Yes
03. Signals |  | X1 mode | X1 mode | User | 0..1 | 0 | NA | 0 = Analog mode 1 = Digital mode | Defines wether output X1 acts on a analog or digital input signal. Analog mode (0) : Output X1 is defined by X1 type Digital mode (1) : Output X1 will reflect the value of Y2_digital when X1Type is defined as Y2 controlled | W | RW | Output Coil | 20 |  | bool | Binary Value | 14 | Present Value | RW | RW | Yes
03. Signals |  | X1 type | X1 type | User | 0..4 | 0 | NA | 0 = Flow 1 = Pressure 2 = Y2 Controlled 3 = Y1 Controlled 4 = RC_SplitRange | Defines the type of output for X1. Flow (0) : representation of the flow measurement Pressure (1) : representation of the differential pressure measurement Y2 Controlled (2) : controlled from an external device like a CO2 sensor (connected to Y2) or set to a value by Y2 digital. Y1 Controlled (3) : representation of Y1 input RC_SplitRange (4) : representation of Y1h and Y1c, calculated by the IRC, in a split-range format for use as Y1 input on slave valves | W | RW | Holding Register | 78 |  | uint | Multistate Value | 11 | Present Value | RW | RW | Yes
03. Signals |  | X1 characteristic | X1char | User | 0..1 | 0 | NA | 0 = Linear 1 = Equal percentage | Defines the representation of the X1 feedback signal. Linear (0) : X1 feedback signal is lineair in relation with the flow Equal percentage (1) : X1 feedback signal is Equal percentage in relation with the flow | W | RW | Holding Register | 72 |  | uint | Multistate Value | 12 | Present Value | RW | RW | Yes
03. Signals |  | Xm Actuator Feedback | Xm | User | 0..10 | NA | Volt (dc) | 0.1 | Reflects the actual actuator feedback signal. Range: 0..10Vdc, representing the current actuator position 0..100% (only applicable when 0..10Vdc drive is used). | V | R | Input Register | 78 |  | uint | Analog Value | 20 | Present Value
03. Signals |  | Xm PWM | Xm PWM | User | 0..200 | NA | % | 1 | PWM duty cycle of thermal motor control signal (only applicable when PWM control) 0..200 = 0..100%. | V | R | Input Register | 71 |  | uint
03. Signals |  | Input Y1 | Y1 | User | Y1min ..Y1max | NA | Volt (dc) | 0.1 | Y1 defines the valve Setpoint. - In Analog mode, it's used to define Y1h or Y1c depending on the Sys Type [NR] - In Digital mode, it's NOT used but it can be read | V | R | Input Register | 69 |  | uint | Analog Input | 6 | Present Value | R | R | Yes
03. Signals |  | Input Y1 Maximum | Y1 max | User | 0..10 | 10 | Volt (dc) | 0.1 | The maximum value of Y1 in case it is not used for setpoint at the flow control loop or IRC-control (for example when used to control X1.) | W | RW | Holding Register | 7 |  | uint |  |  |  | RW | RW | Yes
03. Signals |  | Input Y1 Minimum | Y1 min | User | 0..10 | 2 | Volt (dc) | 0.1 | The minimum value of Y1 in case it is not used for setpoint at the flow control loop or IRC-control (for example when used to control X1.) | W | RW | Holding Register | 6 |  | uint |  |  |  | RW | RW | Yes
03. Signals |  | Input Y2 | Y2 | User | Y2min ..Y2max | NA | Volt (dc) | 0.1 | Corresponds to the voltage level of the input signal Y2, for example of a êp controller. (arvt : moet dit geen dP SENSOR zijn?) | V | R | Input Register | 70 |  | uint | Analog Input | 7 | Present Value | R | R | Yes
03. Signals |  | Input Y2 Maximum | Y2 max | User | 0..10 | 10 | Volt (dc) | 0.1 | The maximum working voltage on Y2. This value can be used with êp controller. | W | RW | Holding Register | 9 |  | uint |  |  |  | RW | RW | Yes
03. Signals |  | Input Y2 Minimum | Y2 min | User | 0..10 | 2 | Volt (dc) | 0.1 | The minimum working voltage on Y2. This value can be used with êp controller. | W | RW | Holding Register | 8 |  | uint |  |  |  | RW | RW | Yes
03. Signals |  | DI1 Type | DI1 Type | User | 0..1 | 0 | NA | 0 = NC 1 = NO | It defines rest status the Digital Input 1 contact. Normally Closed (0) : Default state of input is a closed contact Normally Open (1) : Default state of input is an open contact Note - it has no impact if the Digital input 1 is defined as a counter. | W | RW | Output Coil | 18 |  | bool | Binary Value | 6 | Present Value | RW | RW | Yes
03. Signals |  | DI1 Usage | DI1 Usage | User | 0..8 | 0 | NA | 0 = Not used 1 = Window open 2 = Away mode 3 = Counter 4 = Night mode 5 = Control on max heating 6 = Control on max cooling 8 = Condense | Bits 0x000F of register are used to define DI1 Usage. Not used (0) : Digital Input is not in use Window Open (1) : Digital Input signals state of Open Window, will reflect on SetpModif Away mode (2) : Digital Input signals state of no presence, will reflect on SetpModif Counter (3) : Digital Input counts number of pulses in input Night mode (4) : Digital Input signals state of night mode, will reflect on SetpModif Control Max Heating (5) : Digital Input forces flow control to Vsmaxhd, will reflect on SetpModif Control Max Cooling (6) : Digital Input forces flow control to Vsmaxcd, will reflect on SetpModif Condense (8) : Digital Input signals state of Condensation sensor, will reflect on SetpModif | W | RW | Holding Register | 77 |  | uint | Multistate Value | 5 | Present Value | RW | RW | Yes
03. Signals |  | DI1 Counter | DI1_Counter | User | 0..65535 | 0 | NA | - | Value indicating the total number of pulses for Digital Input 1. Note - Digital Input 1 has to be defined as a counter by DI1 Usage. | W | R | Input Register | 94 |  | uint |  |  |  | R | R | Yes
03. Signals |  | DI1 Active | DI1 Active | User | 0..1 | NA | NA | 0 = Contact NOT active 1 = Contact active | Status of Digital Input 1. Contact NOT active (0) : Contact is in default state Contact active (1) : Contact is NOT in default state Note - Default state is determined by setting of DI1 Type | V | R | Discrete Register | 6 |  | bool | Binary Input | 0 | Present Value | R | R | Yes
03. Signals |  | DI2 Type | DI2 Type | User | 0..1 | 0 | NA | 0 = NC 1 = NO | It defines rest status the Digital Input 2 contact. Normally Closed (0) : Default state of input is a closed contact Normally Open (1) : Default state of input is an open contact Note - it has no impact if the Digital input 2 is defined as a counter. | W | RW | Output Coil | 19 |  | bool | Binary Value | 7 | Present Value | RW | RW | Yes
03. Signals |  | DI2 Usage | DI2 Usage | User | 0..8 | 0 | NA | 0 = Not used 1 = Window open 2 = Away mode 3 = Counter 4 = Night mode 5 = Control on max heating 6 = Control on max cooling 8 = Condense | Bits 0x00F0 of register are used to define DI2 Usage. Not used (0) : Digital Input is not in use Window Open (1) : Digital Input signals state of Open Window, will reflect on SetpModif Away mode (2) : Digital Input signals state of no presence, will reflect on SetpModif Counter (3) : Digital Input counts number of pulses in input Night mode (4) : Digital Input signals state of night mode, will reflect on SetpModif Control Max Heating (5) : Digital Input forces flow control to Vsmaxhd, will reflect on SetpModif Control Max Cooling (6) : Digital Input forces flow control to Vsmaxcd, will reflect on SetpModif Condense (8) : Digital Input signals state of Condensation sensor, will reflect on SetpModif | W | RW | Holding Register | 77 |  | uint | Multistate Value | 6 | Present Value | RW | RW | Yes
03. Signals |  | DI2 Counter | DI2_Counter | User | 0..65535 | 0 | NA | - | Value indicating the total number of pulses for Digital Input 2. Note - Digital Input 2 has to be defined as a counter by DI2 Usage. | W | R | Input Register | 95 |  | uint |  |  |  | R | R | Yes
03. Signals |  | DI2 Active | DI2Active | User | 0..1 | NA | NA | 0 = Contact NOT active 1 = Contact active | Status of Digital Input 2. Contact NOT active (0) : Contact is in default state Contact active (1) : Contact is NOT in default state Note - Default state is determined by setting of DI2 Type | V | R | Discrete Register | 7 |  | bool | Binary Input | 1 | Present Value | R | R | Yes
03. Signals |  | DI3 Type | DI3 Type | User | 0..1 | 0 | NA | 0 = NC 1 = NO | It defines the digital input 3 contact has normally open or normally closed. It has no impact if the digital input 3 is defined as a counter. | W | RW | Output Coil | 24 |  | bool | Binary Value | 13 | Present Value | RW | RW | Yes
03. Signals |  | DI3 Usage | DI3 Usage | User | 0..8 | 0 | NA | 0 = Not used 1 = Window open 2 = Away mode 3 = Counter 4 = Night mode 5 = Control on max heating 6 = Control on max cooling 8 = Condense | Bits 0x0F00 of register are used to define DI3 Usage. Not used (0) : Digital Input is not in use Window Open (1) : Digital Input signals state of Open Window, will reflect on SetpModif Away mode (2) : Digital Input signals state of no presence, will reflect on SetpModif Counter (3) : Digital Input counts number of pulses in input Night mode (4) : Digital Input signals state of night mode, will reflect on SetpModif Control Max Heating (5) : Digital Input forces flow control to Vsmaxhd, will reflect on SetpModif Control Max Cooling (6) : Digital Input forces flow control to Vsmaxcd, will reflect on SetpModif Condense (8) : Digital Input signals state of Condensation sensor, will reflect on SetpModif | W | RW | Holding Register | 77 |  | uint | Multistate Value | 8 | Present Value | RW | RW | Yes
03. Signals |  | DI3 Counter | DI3_Counter | User | 0..65535 | 0 | NA | - | Value indicating the total number of pulses for Digital Input 3. Note - Digital Input 3 has to be defined as a counter by DI3 Usage. | W | R | Input Register | 143 |  | uint |  |  |  | R | R | Yes
03. Signals |  | DI3 Active | DI3Active | User | 0..1 | NA | NA | 0 = Contact NOT active 1 = Contact active | Status of Digital Input 3. Contact NOT active (0) : Contact is in default state Contact active (1) : Contact is NOT in default state Note - Default state is determined by setting of DI3 Type | V | R | Discrete Register | 8 |  | bool | Binary Input | 2 | Present Value | R | R | Yes
03. Signals |  | Y2 digital Setpoint | Y2 digital | User | Y2min ..Y2max | 0 | Volt (dc) | 0.1 | Setpoint voltage to control X1 output in digital mode. If the user defines the X1 Type as "Y2 controlled" and the X1 mode as "Digital", then Y2 digital will be reflected on X1 output. | W | RW | Holding Register | 79 |  | uint | Analog Value | 16 | Present Value | RW | RW | Yes
03. Signals |  | External Temperature Sensor 1 Measurement | Text 1 | User | 0..65535 | NA | °C/°F | 0.1 | Value of external temperature measurement Text1. Sensor type is defined by Text1 Type (PT500, PT1000 or Res10K). | V | R | Input Register | 91 |  | uint | Analog Input | 4 | Present Value | R | R | Yes
03. Signals |  | External Temperature Sensor 2 Measurement | Text 2 | User | 0..65535 | NA | °C/°F | 0.1 | Value of external temperature measurement Text2. Sensor type is defined by Text2 Type (PT500, PT1000 or Res10K). | V | R | Input Register | 92 |  | uint | Analog Input | 5 | Present Value | R | R | Yes
03. Signals |  | External Temperature Sensor 1 Type | Text1 Type | User | 0..2 | 1 | bit field | NA | Bits 0x000F of register are used as a bit field to define Text1 resistive type. bit 0: a Pt500 resistor is used for temperature measurement. bit 1: a Pt1000 resistor is used for temperature measurement. bit 2: a 10K ohm potentiometer is used for setting of Tsetadj Note - use of a Pt500 sensor only applies on CB3-generation valves | W | RW | Holding Register | 69 |  | sint | Multistate Value | 9 | Present Value | RW | RW | Yes
03. Signals |  | External Temperature Sensor 2 Type | Text2 Type | User | 0..2 | 1 | bitfield | NA | Bits 0x00F0 of register are used as a bit field to define Text2 resistive type. bit 0: a Pt500 resistor is used for temperature measurement. bit 1: a Pt1000 resistor is used for temperature measurement. bit 2: a 10K ohm potentiometer is used for setting of Tsetadj Note - use of a Pt500 sensor only applies on CB3-generation valves | W | RW | Holding Register | 69 |  | sint | Multistate Value | 10 | Present Value | RW | RW | Yes
04. |  | Modbus 32b Long Endianness | Long_Endianness | User | 0..1 | 1 | NA | 0= Little Endian 1 = Big Endian | Sets the representation format of 32 bits values in Modbus Little Endian (0) : output of 32 bit values as Little Endian (backwards compatibility) Big Endian (1) : output of 32 bit values as Big Endian | W | RW | Output Coil | 12 |  | bool |  |  |  | RW | RW | Yes
04.Status |  | BACNet Network Address | BACNet_NetwAddr | User | 0..65534 | 0 | NA | 1 | Sets the BACnet Network Number for the RS485 communication. | W | RW | Holding Register | 84 |  | uint
04.Status |  | Communication Baudrate | Baudrate | User | 0..2 | 2 | NA | 0 = 9600 bit/s 1 = 19200 bit/s 2 = 38400 bit/s | Sets the Baudrate for the RS485 communication. 9600 bit/s (0) : sets communication speed at 9600 19200 bit/s (1) : sets communication speed at 19k2 38400 bit/s (2) : sets communication speed at 38k4 Note - If changed, the devices will reboot and starts operating with the new baud rate. | W | RW | Holding Register | 5 |  | uint | Network Port | - | - | RW | RW | Yes
04.Status |  | Display ON | Display ON | Factory | 0..1 | 0 | NA | 0 = LCD Off (1 min delay) 1 = LCD On | Configures the behaviour of the LCD display LCD Off (0) : the LCD switches off after 1 min of being on LCD On (1) : the LCD stays on permanently Note - setting only applies on CB3-generation valves whit LCD present | W | RW | Output Coil | 9 |  | bool
04.Status |  | Error | Error | User | 0..255 | NA | NA | 0 = no error ≠0 = error, according to bit field | Refer to the corresponding section in user manual | V | R | Input Register | 60 |  | uint | Analog Input | 9 | Present Value | R | R | Yes
04.Status |  | Error2 | Error2 | User | 0..255 | NA | NA | 0 = no error ≠0 = error, according to bit field | Refer to the corresponding section in user manual | V | R | Input Register | 150 |  | uint32 | Analog Input | 11 | Present Value | R | R | Yes
04.Status |  | Communication Address | Address | User | 0..247 | 247 (Modbus) 127 (BACNet) | NA | 1..247 (Modbus) 1..127 (BACNet) | Sets the Slave Address for the RS485 communication. | W | RW | Holding Register | 18 |  | uint | Network Port | - | - | RW | RW | Yes
04.Status |  | Communication Parity | Parity | User | 0..2 | 2 | NA | 0 = no parity 1 = odd parity 2 = even parity | Sets the Parity for the RS485 communication. no parity (0) odd parity (1) even parity (2) Note - Only applies for Modbus communication. | W | RW | Holding Register | 24 |  | uint |  |  |  | RW | RW | Yes
04.Status |  | Port1 Active | Port1Active | User | 0..1 | 0 | NA | 0 = port 2 active 1 = port 1 active | Information on which port is in use on 6-port valve. port 2 active (0) : Port 2 is active port 1 active (1) : Port 1 is active Note - this register is used only with 6-port valves (DXN6). | W | R | Discrete Register | 5 |  | bool |  |  |  | R | R | Yes
04.Status |  | Protocol | Protocol | User | 1..2 | 1 | NA | 1 = MODBUS 2 = BACNet | Shows which communication protocol is being used. MODBUS (1) : RS485 communication is Modbus-RTU BACNet (2) : RS485 communication is BACNet MSTP | W | R | Input Register | 144 |  | uint32 |  |  |  | R | R | Yes
04.Status |  | Reboot | Reboot | User | 0..1 | 0 | NA | 1 to reboot system | Reboots the system: clearing all volatile variables. Note - Automatically resets to 0. | V | RW | Output Coil | 1 |  | bool | Binary Value | 12 | Present Value | RW | RW | Yes
04.Status |  | Reset | Reset | User | 0..1 | 0 | NA | 1 to reset system | Resets the system: clearing all volatile variables, except the reboot counters and registers. Note - Automatically resets to 0. | V | RW | Output Coil | 2 |  | bool |  |  |  | RW | RW | Yes
04.Status |  | Values Modbus Based | ValModbusBased | User | 0..1 | 0 | NA | 0 = BACnet obj starts at 1 1 = BACnet obj starts at 0 | Defines the start address of the MultiState values in BACNET BACnet obj starts at 1 (0) : Object numbers MultiState starts at 1 BACnet obj starts at 0 (1) : numbering follows MODBUS list and starts at 0 | W | RW | Output Coil | 25 |  | bool | Binary Value | 15 | Present Value
04.Status |  | Warning | Warning | User | 0..255 | NA | NA | 0 = no warning ≠0 = warning, according to bit field | Refer to the corresponding section in user manual | V | R | Input Register | 61 |  | uint | Analog Input | 8 | Present Value | R | R | Yes
04.Status |  | Warning2 | Warning2 | User | 0..255 | NA | NA | 0 = no warning ≠0 = warning, according to bit field | Refer to the corresponding section in user manual | V | R | Input Register | 151 |  | uint32 | Analog Input | 10 | Present Value | R | R | Yes
04.Status |  | Days of Operation | Days oper | User | 0..65535 | NA | Days | 1 | Total days in operation since first power-up | W | R | Input Register | 68 |  | uint |  |  |  | R | R | Yes
04.Status |  | Time after last reboot (hours) | hh reb | User | 0..65535 | NA | Hours | 1 | Hours since system-reboot (power-up or software-reboot) | V | R | Input Register | 65 |  | uint |  |  |  | R | R | Yes
04.Status |  | Time after last reboot (minutes) | mm reb | User | 0..59 | NA | Minutes | 1 | Minutes since system-reboot (power-up or software-reboot) | V | R | Input Register | 66 |  | uint |  |  |  | R | R | Yes
04.Status |  | Time after last reboot (seconds) | ss reb | User | 0..59 | NA | Seconds | 1 | Seconds since system-reboot (power-up or software-reboot) | V | R | Input Register | 67 |  | uint |  |  |  | R | R | Yes
05. Energy |  | External Temperature Sensor | T ext | User | 0° .. + 90° | NA | °C/°F | 0.1 | Actual medium temperature from an external sensor. Reporting Unit can be °C or °F, depending on value of Tunit. Note - Only used when 2nd temperature sensor is NOT present. | W | RW | Holding Register | 19 | 20 | uint32
05. Energy |  | Temperature Sensor Offset | T off | User | -9°C .. + 9°C -16.2°F.. +16.2°F | 0 | °C/°F | 0.1 | Offset temperature correction between 2 sensors. Reporting Unit can be °C or °F, depending on value of Tunit. Note - Only valid when 2 sensors are used. | W | RW | Holding Register | 45 | 46 | uint32
05. Energy |  | Temperature Units | T unit | User | 0..1 | 0 | NA | 0 = °C 1 = °F | Sets the representation format of all temperature variables to Celsius or Fahrenheid °C (0) : All variables used in degrees Celsius °F (1) : All variables used in degrees Fahrenheid | W | RW | Output Coil | 3 |  | bool | Binary Value | 16 | Present Value | RW | RW | Yes
05. Energy |  | Temperature Sensor1 Correction | T1_Correction | User | -5..5°C | 0°C | °C/°F | 0.1 | Temperature correction for Temperature sensor T.ext1 | W | RW | Holding Register | 88 |  | uint | Analog Value | 21 | Present Value | RW | RW | Yes
05. Energy |  | Temperature Sensor2 Correction | T2_Correction | User | -5..5°C | 0°C | °C/°F | 0.1 | Temperature correction for Temperature sensor T.ext2 | W | RW | Holding Register | 89 |  | uint | Analog Value | 22 | Present Value | RW | RW | Yes
05. Energy |  | Actuel Medium Temperature 1 | Tam 1 | User | 0° .. + 90° | NA | °C/°F | 0.1 | Reflects the actual medium temperature, measured by sensor Tam1. Reporting Unit can be °C or °F, depending on value of Tunit. | V | R | Input Register | 100 | 101 | float | Analog Input | 1 | Present Value | R | R | Yes
05. Energy |  | Actuel Medium Temperature 2 | Tam 2 | User | 0° .. + 90° | NA | °C/°F | 0.1 | Reflects the actual medium temperature, measured by sensor Tam2. Reporting Unit can be °C or °F, depending on value of Tunit. | V | R | Input Register | 102 | 103 | float | Analog Input | 2 | Present Value | R | R | Yes
05. Energy |  | Energy Counter Units | E unit | User | 0..1 | 0 (SI and UK) 1 (US) | NA | 0 = Wh 1 = BTU | Unit for cumulative energy consumption. Wh (0) : energy consumption presented in Wh BTU (1) : energy consumption presented in BTU Note - resolution depends on Vrange | W | RW | Holding Register | 47 |  | uint |  |  |  | RW | RW | Yes
05. Energy |  | Energy Counter Cooling | Ener. cool | User | Wh:0 .. 4294967295 BTU: 0 .. 1465503606 | NA | kWh/BTU | depending on Vrange | Cumulative energy consumption in Climate Status Cooling mode. For more detailed information, follow the link to the Energy & Power Table. Note - resolution depends on Vrange | W | R | Input Register | 132 | 133 | uint32 | Analog Value | 11 | Present Value | R | R | Yes
05. Energy |  | Energy Counter Heating | Ener. heat | User | Wh:0 .. 4294967295 BTU: 0 .. 1465503606 | NA | kWh/BTU | depending on Vrange | Cumulative energy consumption in Climate Status Heating mode. For more detailed information, follow the link to the Energy & Power Table. Note - resolution depends on Vrange | W | R | Input Register | 130 | 131 | uint32 | Analog Value | 10 | Present Value | R | R | Yes
05. Energy |  | Current Power | PWR | User | 0..65535 | NA | Watt | 1 | Power consumption (If PWR = 0xFFFF, error). For more detailed information, follow the link to the Energy & Power Table. | V | R | Input Register | 55 |  | uint | Analog Value | 30 | Present Value | R | R | Yes
Flow control |  | Phi | Phi | Factory | 0..100 | NA | NA | 0.01 | Equal percentage curvature | W | RW | Holding Register | 38 |  | sint
Flow control |  | Setpoint Modification | Setp modif | User | NA | 0 | bitfield | NA | Bitfield which represents the different states, set by digital inputs or over the bus, that can effect the IRC or flow setpoint. bit 0: window open bit 1: away mode bit 2: night mode bit 3: condensation bit 4: frost protection bit 5: control max heating bit 6: control max cooling | V | R | Input Register | 87 |  | uint | Analog Value | 6 | Present Value | RW | RW | Yes
Flow control |  | Flow Units | V unit | User | 0..4 | SI = 0 UK = 3 US = 4 | NA | 0 = m³/h 1 = l/s 2 = l/min 3 = Gpm (UK) 4 = Gpm (US) | Reporting unit of flow parameters. m³/h (0) : Flow values are presented in m3/h l/s (1) : Flow values are presented in l/s l/min (2) : Flow values are presented in l/min Gpm (UK) (3) : Flow values are presented in Gpm Gpm (US) (4) : Flow values are presented in Gpm Note - Default depends on product version. | W | RW | Holding Register | 4 |  | uint |  |  |  | RW | RW | Yes
Flow control |  | Nominal Flow Cooling | Vnomc | User | Type dependent | NA | cf. Vunit | NA (floating point) | Nominal flow for cooling. Is factory set to the highest flow the device can cope with. | C | R | Input Register | 116 | 117 | float
Flow control |  | Nominal Flow Heating | Vnomh | User | Type dependent | NA | cf. Vunit | NA (floating point) | Nominal flow for heating. Is factory set to the highest flow the device can cope with. | C | R | Input Register | 114 | 115 | float
Flow control |  | Flow Setpoint Cooling Maximum | Vs maxc d | User | Vsmincd..Vnomc | Vnomc | cf. Vunit | Depend on Vunit and Vrange | Setpoint for the maximum calculated flow in Climate Status Cooling mode. Note - Will always mirror Vsmincd. | W | RW | Holding Register | 44 |  | uint | Analog Value | 3 | High Limit | RW | RW | Yes
Flow control |  | Flow Setpoint Heating Maximum | Vs maxh d | User | Vsminhd..Vnomh | Vnomh | cf. Vunit | Depend on Vunit and Vrange | Setpoint for the maximum calculated flow in Climate Status Heating mode. Note - Will always mirror Vsminhd. | W | RW | Holding Register | 43 |  | uint | Analog Value | 2 | High Limit | RW | RW | Yes
Flow control |  | Flow Setpoint Cooling Minimum | Vs minc d | User | 0..Vsmaxcd | 0 | cf. Vunit | Depend on Vunit and Vrange | Setpoint for the minimum calculated flow in Climate Status Cooling mode. | W | RW | Holding Register | 42 |  | uint | Analog Value | 3 | Low Limit | RW | RW | Yes
Flow control |  | Flow Setpoint Heating Minimum | Vs minh d | User | 0..Vsmaxhd | 0 | cf. Vunit | Depend on Vunit and Vrange | Setpoint for the minimum calculated flow in Climate Status Heating mode. | W | RW | Holding Register | 41 |  | uint | Analog Value | 2 | Low Limit | RW | RW | Yes
Flow control |  | Flow Setpoint Cooling | Vsc | User | Type dependent | NA | cf. Vunit | Depend on Vunit and Vrange | Reflects the calculated flow setpoint when Climate Status is in Cooling mode. | W | RW | Holding Register | 33 |  | uint | Analog Value | 3 | Present Value | RW | RW | Yes
Flow control |  | Flow Setpoint Heating | Vsh | User | Type dependent | NA | cf. Vunit | Depend on Vunit and Vrange | Reflects the calculated flow setpoint when Climate Status is in Heating mode. | W | RW | Holding Register | 32 |  | uint | Analog Value | 2 | Present Value | RW | RW | Yes
Flow control |  | Qp | Qp | Factory | 0.6..40 | NA | m³/h | 0.1 | Nominal flow of the flow sensor. | C | R | Input Register | 52 |  | uint
Flow control |  | Flow Measurement (filtered) | Vam | User | Type dependent | NA | cf. Vunit | NA (floating point) | Represents the actual medium flow measured by the device. Vam is reported in the unit defined by Vunit. The range (number of decimals) is defined by Vrange. | V | R | Input Register | 108 | 109 | float | Analog Input | 0 | Present Value | R | R | Yes
Flow control |  | Flow Measurement (real/unfiltered) | Vr | User | Type dependent | NA | cf. Vunit | NA (floating point) | Represents the real medium flow. Vr is filtered to derive Vam, which fluctuates a lot less than Vr. When there's a new setpoint, then Vam = Vr. When Vr reaches Vs a first order filter is applied on Vam until the setpoint is changed again. Vr is reported in the unit defined by Vunit. The range (number of decimals) is defined by Vrange. | V | R | Input Register | 106 | 107 | float | Analog Input | 12 | Present Value
Flow control |  | End Mode Behavior | EndMode | User | 0..2 | 0 | NA | 0 = Normal behavior 1 = No flow 2 = Flush mode | The EndMode will define how the valve should react if the analog input Y1 is set in the range [ 0V - 0.2V ] or [ 9.8V - 10V ]. Normal behavior (0) : the flow setpoint will follow Vsmaxcd or Vsmaxhd. No flow (1) : the valve will be closed (center position). Flush mode (2) : the valve will open completely to the corresponding port (for example when Y1 is set to 0V and 0.5 to 4.5 set as boundaries for heating, the valve will open completely to the correspondent heating port). Note - this register used only with 6-port valves (DXN6) with analog Control Signal. | W | RW | Holding Register | 75 |  | uint |  |  |  | RW | RW | Yes
Flow control |  | Y1 Maximum Cooling Setpoint | Y1 maxc | User | 0..10 | 10 | Volt (dc) | 0.1 | The value of Y1c at which the flow control loop still operates. The flowsetpoint for cooling Vsc will be equal to Vsmaxcd. | W | RW | Holding Register | 31 |  | uint | Analog Value | 1 | High Limit | RW | RW | Yes
Flow control |  | Y1 Maximum Heating Setpoint | Y1 maxh | User | 0..10 | 10 | Volt (dc) | 0.1 | The value of Y1h at which the flow control loop still operates. The flowsetpoint for heating Vsh will be equal to Vsmaxhd. | W | RW | Holding Register | 30 |  | uint | Analog Value | 0 | High Limit | RW | RW | Yes
Flow control |  | Y1 Minimum Cooling Setpoint | Y1 minc | User | 0..10 | 2 | Volt (dc) | 0.1 | The value of Y1c at which the flow control loop starts to operate. The flowsetpoint for cooling Vsc will be equal to Vsmincd. | W | RW | Holding Register | 29 |  | uint | Analog Value | 1 | Low Limit | RW | RW | Yes
Flow control |  | Y1 Minimum Heating Setpoint | Y1 minh | User | 0..10 | 2 | Volt (dc) | 0.1 | The value of Y1h at which the flow control loop starts to operate. The flowsetpoint for heating Vsh will be equal to Vsminhd. | W | RW | Holding Register | 28 |  | uint | Analog Value | 0 | Low Limit | RW | RW | Yes
Flow control |  | Y1 Cooling Setpoint | Y1c | User | Y1minc .. Y1maxc | NA | Volt (dc) | 0.1 | Reflects the current setpoint for cooling Vsc. - In digital mode this is a read-write parameter. - In analog mode it is set by the external analog input signal Y1 and read-only on the UI and bus. | W | RW | Holding Register | 27 |  | uint | Analog Value | 1 | Present Value | RW | RW | Yes
Flow control |  | Y1 Heating Setpoint | Y1h | User | Y1minh .. Y1maxh | NA | Volt (dc) | 0.1 | Reflects the current setpoint for heating Vsh. - In digital mode this is a read-write parameter. - In analog mode it is set by the external analog input signal Y1 and read-only on the UI and bus. | W | RW | Holding Register | 26 |  | uint | Analog Value | 0 | Present Value | RW | RW | Yes
IRC / ICT Ctrl |  | Room Controller Type | RCtype | User | 0 .. 1 | 0 (P) | NA | 0 (P) 1 (PI) | Defines the control type of the integrated room controller. P (0) : IRC is P-controlled PI (1) : IRC is PI-controlled | W | RW | Holding Register | 59 |  | uint | Multistate Value | 13 | Present Value | RW | RW | Yes
IRC / ICT Ctrl |  | Temperature Controller Dead band | Td | User | 0.2 .. 6°C | 1°C | °C or °F, depending on Tunit | 0.1°C | Controller dead band between heating and cooling | W | RW | Holding Register | 53 |  | uint | Analog Value | 23 | Present Value | RW | RW | Yes
IRC / ICT Ctrl |  | Temperature Controller Dead band (Night mode) | Tdnight | User | 0.2..20ºC | 20°C | °C or °F, depending on Tunit | 0.1°C | Controller dead band between heating and cooling in Night mode | W | RW | Holding Register | 60 |  | uint | Analog Value | 24 | Present Value | RW | RW | Yes
IRC / ICT Ctrl |  | Temperature High Limit Window Open | Twindhigh | User | 6..40°C | 40°C | °C or °F, depending on Tunit | 0.1°C | In window open mode the temperature setpoint Tsetcalc for cooling is set to Twindhigh. Note - Window Open mode can be activated by a digital input and status can be seen in Setp modif | W | RW | Holding Register | 58 |  | uint | Analog Value | 26 | Present Value | RW | RW | Yes | IRC
IRC / ICT Ctrl |  | Temperature Low Limit Window Open | Twindlow | User | 6..35°C | 15°C | °C or °F, depending on Tunit | 0.1°C | In window open mode the temperature setpoint Tsetcalc for heating is set to Twindlow. Note - Window Open mode can be activated by a digital input and status can be seen in Setp modif | W | RW | Holding Register | 57 |  | uint | Analog Value | 25 | Present Value | RW | RW | Yes | ITC
IRC / ICT Ctrl |  | Cooling Active | CoolActive | User | 0..1 | NA | NA | 0 = cooling flow closed 1 = cooling flow open | Reflects whether the room controller is cooling the room Cooling flow closed (0) : No cooling water goes through the valve Cooling flow open (1) : Cooling water goes through the valve | V | R | Discrete Register | 4 |  | bool
IRC / ICT Ctrl |  | Frost Protection Enable | FrostEnable | User | 0..1 | 1 | NA | 0 = disabled 1 = enabled | Enables or disables frost protection based on Troom Disabled (0) : No frost protection Enabled (1) : When Troom is lower then 6°C, heating will be activated | V | RW | Output Coil | 21 |  | bool | Binary Value | 17 | Present Value | RW | RW | Yes
IRC / ICT Ctrl |  | Heating Active | HeatActive | User | 0..1 | NA | NA | 0 = heating flow closed 1 = heating flow open | Reflects whether the room controller is heating the room Heating flow closed (0) : No heating water goes through the valve Heating flow open (1) : Heating water goes through the valve | V | R | Discrete Register | 3 |  | bool
IRC / ICT Ctrl |  | Night mode | Night mode | User | 0..1 | 0 | NA | 0 = disabled 1 = enabled | Enables or disables Night mode for the IRC Disabled (0) : Night mode is not active, dead band for controller is set to Td Enabled (1) : Night mode is active, dead band for controller is set to Tdnight Note - Night mode can be activated by a digital input or over Modbus/BACNet | V | RW | Output Coil | 11 |  | bool | Binary Value | 4 | Present Value | RW | RW | Yes
IRC / ICT Ctrl |  | Pband Cooling | Pbandcool | User | 0.5 .. 6°C | 2°C | °C or °F, depending on Tunit | 0.1°C | Width of proportional band for cooling | W | RW | Holding Register | 55 |  | uint | Analog Value | 28 | Present Value | RW | RW | Yes
IRC / ICT Ctrl |  | Pband Heating | Pbandheat | User | 0.5 .. 6°C | 1°C | °C or °F, depending on Tunit | 0.1°C | Width of proportional band for heating | W | RW | Holding Register | 54 |  | uint | Analog Value | 27 | Present Value | RW | RW | Yes
IRC / ICT Ctrl |  | Room Temperature Cooling Minimum | Tcoolmin | User | 9..35°C | 9°C | °C/°F | 0.1 | If the cooling setpoint Tsetcalc + Td falls below Tcoolmin, then Tcoolmin is taken as the actual cooling setpoint. | W | RW | Holding Register | 61 |  | uint | Analog Value | 7 | Present Value | RW | RW | Yes
IRC / ICT Ctrl |  | Room Temperature Measurement | Troom | User | Troom min .. Troom max | Tsetcalc | °C/°F | 0.1 | Actual room temperature Note - For temperature controled ITC C03/C04 Troom represend the actual medium temperature | V(Analog) / W(Digital) | R | Holding Register | 50 |  | uint | Analog Value | 12 | Present Value | RW | RW | Yes
IRC / ICT Ctrl |  | Room Temperature Maximum | Troom max | User | 0..90°C | 90°C | °C/°F | 0.1 | Value determins the maximum value when Troom measurement is read from input Y1. (Troom for Y1=10V) | W | RW | Holding Register | 82 |  | uint | Analog Value | 12 | High Limit | RW | RW | Yes
IRC / ICT Ctrl |  | Room Temperature Minimum | Troom min | User | 0..90°C | 0 | °C/°F | 0.1 | Value determins the minimum value when Troom measurement is read from input Y1. (Troom for Y1=0V) | W | RW | Holding Register | 81 |  | uint | Analog Value | 12 | Low Limit | RW | RW | Yes
IRC / ICT Ctrl |  | IRC/ITC Temperature Setpoint | Tset | User | 14..35°C | 22°C | °C/°F | 0.1 | Room temperature setpoint | V(Analog / W(Digital) | RW | Holding Register | 51 |  | uint | Analog Value | 4 | Present Value | RW | RW | Yes
IRC / ICT Ctrl |  | Room Temperature Setpoint Adjustment | Tsetadj | User | -TsetadjMax..TsetadjMax | 0°C | °C/°F | 0.1 | Room temperature setpoint adjustment. When Ctrl Sig is Analog, Tsetadj is determined by T.ext1, when Ctrl Sig is Digital, Tsetadj can be written over the RS485 bus | W | RW | Holding Register | 52 |  | int | Analog Value | 13 | Present Value | RW | RW | Yes
IRC / ICT Ctrl |  | Maximum Setpoint Adjustment | TsetadjMax | User | 0..5°C | 5°C | °C/°F | 0.1 | This settings determines the maximum value for Tsetadj. Tsetadj will be between -TsetadjMax and + TsetadjMax. | W | RW | Holding Register | 80 |  | uint | Analog Value | 13 | High Limit | RW | RW | Yes
IRC / ICT Ctrl |  | Room Temperature Calculated Setpoint | Tsetcalc | User | 9..40°C | NA | °C/°F | 0.1 | Calculated Room temperature setpoint. Tsetcalc = Tset+Tsetadj | V | R | Input Register | 86 |  | uint | Analog Value | 5 | Present Value | R | R | Yes
Warning! Type W variables are written in non-volatile memory. It should be noted that non-volatile memory is limited by the number of writing cycles after which it becomes dysfunctional. Therefore non-volatile memory is typically used for parameter setting only. This value is not expected to change over the lifetime of the device. An example may be the MODBUS baud rate. If the application would require frequent writing however, it is strongly recommended to drastically limit the frequency of writing new values in the non-volatile memory. A value should not be written to the non-volatile memory more than 4x per day. Surpassing the number of writing cycles to the non-volatile memory voids the warranty.
Waarschuwing! Informatie over het gebruik van variabelen die in het EEPROM geheugen worden opgeslagen. Als uitgangspunt kan de levensduur van de EEPROM worden geschat op 100.000 schrijfcycli. Merk op dat dit gebaseerd is op 100k schrijfcycli MINIMAAL. Het is mogelijk dat de EEPROM (iets) langer meegaat, maar dit hangt af van verschillende factoren (temperatuur, kwaliteit van het IC, ...). De variabelen type ‘W’ worden opgeslagen in de EEPROM. De waarden type ‘V’ (bijvoorbeeld Y1h en Y1c) zijn echter NIET opgeslagen in de EEPROM en kunnen worden geschreven zonder limiet. Waarden worden in EEPROM opgeslagen indien: 1. Ze worden geschreven via de bus of via de APP, naar het holding register. Als bijvoorbeeld Tsetadj wordt afgelezen via de potentiometeringang van de ruimtesensor en de waarde wordt telkens geactualiseerd, dan is dat niet het geval. 2. Waarden die in de EEPROM worden opgeslagen, d.w.z. wanneer zij naar het holding register worden geschreven, zal de firmware van de regelafsluiter deze eerst vergelijken met de waarde die reeds in de EEPROM is opgeslagen. Als het dezelfde is, wordt deze waarde niet opnieuw geschreven met dezelfde waarde. Alleen als de nieuwe waarde anders is, zal de EEPROM het overnemen en terugschrijven.
Attention! Les variables de type W sont écrites dans une mémoire non volatile. Il convient de noter que la mémoire non volatile est limitée par le nombre de cycles d'écriture après quoi elle deviendra obsolète. D’une manière générale, la mémoire non volatile est utilisée uniquement pour le paramétrage. Il n’est pas prévu de modifier cette valeur au cours de la durée de vie de l'appareil. Prenons un exemple concret : la vitesse de transmission MODBUS. Si l'application exige une écriture fréquente de cette vitesse, il est fortement recommandé de limiter de manière significative la fréquence d’écriture de nouvelles valeurs dans la mémoire non-volatile. Une valeur mémoire non volatile ne peut être écrite plus de quatre fois par jour. En dépassant le cycle de vie de la mémoire non volatile vous annulez tout garantie liée au produit.
Warnung! Variablen vom Typ W werden in einen nichtflüchtigen Speicher geschrieben. Es ist zu beachten, dass der nichtflüchtige Speicher durch die Anzahl der Schreibzyklen begrenzt ist, nach denen er nicht mehr funktioniert. Daher wird der nichtflüchtige Speicher normalerweise nur zur Parametereinstellung verwendet. Es wird nicht erwartet, dass sich dieser Wert während der Lebensdauer des Geräts ändert. Ein Beispiel kann die MODBUS-Baudrate sein. Wenn die Anwendung jedoch häufiges Schreiben erfordern würde, wird dringend empfohlen, die Häufigkeit des Schreibens neuer Werte in den nichtflüchtigen Speicher drastisch zu begrenzen. Ein Wert sollte nicht mehr als 4x pro Tag in den nichtflüchtigen Speicher geschrieben werden. Wenn die Anzahl der Schreibzyklen in den nichtflüchtigen Speicher überschritten wird, erlischt die Garantie.
Note on H137: Arjan van Tilburg: 14-07-2023: opmerking van Gert dat deze waarde ook groter kan zijn als het om een watertemperatuurregeling gaat. Nog controleren en aanvullen

## Vrange Table
Vrange Table
|  | Flow (m3/h) Vunit = 0 | Flow (l/s) Vunit = 1 | Flow (l/min) Vunit = 2
Type | Vrange | dec | dec | dec
DXC2_ | 0 | 0.0001 | 0.0001 | 0.01
DXMB2D015_ | 1 | 0.001 | 0.001 | 0.01
DXMB2D020_ | 1 | 0.001 | 0.001 | 0.01
DXMB2D025_ | 1 | 0.001 | 0.001 | 0.01
DXMB2D032_ | 1 | 0.001 | 0.001 | 0.01
DXMB2D040_ | 2 | 0.001 | 0.001 | 0.1
DXMB2D050_ | 2 | 0.001 | 0.001 | 0.1
DXMB3D015_ | 1 | 0.001 | 0.001 | 0.01
DXMB3D020_ | 1 | 0.001 | 0.001 | 0.01
DXMB3D025_ | 1 | 0.001 | 0.001 | 0.01
DXMB3D032_ | 1 | 0.001 | 0.001 | 0.01
DXMB3D040_ | 2 | 0.001 | 0.001 | 0.1
DXMB3D050_ | 2 | 0.001 | 0.001 | 0.1
DXN6_ | 0 | 0.0001 | 0.0001 | 0.01
DXU2F050_ | 2 | 0.001 | 0.001 | 0.1
DXU2F065_ | 2 | 0.001 | 0.001 | 0.1
DXU2F080_ | 3 | 0.01 | 0.01 | 0.1
DXU2F100_ | 3 | 0.01 | 0.01 | 0.1
DXU2F125_ | 3 | 0.01 | 0.01 | 0.1
DXU2F150_ | 4 | 0.1 | 0.1 | 1
DXU3F050_ | 2 | 0.001 | 0.001 | 0.1
DXU3F065_ | 2 | 0.001 | 0.001 | 0.1
DXU3F080_ | 3 | 0.01 | 0.01 | 0.1
DXU3F100_ | 3 | 0.01 | 0.01 | 0.1
DXU3F125_ | 3 | 0.01 | 0.01 | 0.1
DXU3F150_ | 4 | 0.1 | 0.1 | 1

## Energy & Power Table
Energy counters / Power
Energy counters |  | Power
in Wh | in kWh | in kW
1 | 0.001 | 0.001
1 | 0.001 | 0.001
10 | 0.01 | 0.01
10 | 0.01 | 0.01
10 | 0.01 | 0.01
10 | 0.01 | 0.01
10 | 0.01 | 0.1
10 | 0.01 | 0.1
10 | 0.01 | 0.1
10 | 0.01 | 0.1
10 | 0.01 | 0.1
10 | 0.01 | 0.1
100 | 0.1 | 0.1
100 | 0.1 | 0.1
100 | 0.1 | 0.1
100 | 0.1 | 0.1
100 | 0.1 | 0.1
100 | 0.1 | 0.1
100 | 0.1 | 1
100 | 0.1 | 1